## Slide 1: ACLAD Operations 2/12/2024
Regular Maintenance
  Repaired 4 major drain line breaks due to land movement with expansion joints
  R&R Well 3, 17
  Fixed WW 11 main breaker
New RPV Wells
  Drilled and developed wells 9, 18, 19, 20
  Installed drain and electric lines to 18 and 20
  WW 18 & 20 pump install this week
  Working with RPV & SCE to energize wells
New ACLAD Wells
  Two new wells drilled and developed
  Working on drains and power
Completed PVDS Culvert repair
Meeting and Tour with LA Stormwater Engineering re: Altamira Canyon
  Presentation Canyon issues at City Hall
  Driving/walking tour of Altamira Canyon from ocean to upper Narcissa
CURRENTLY PUMPING ~130K GPD
  Average output lower due to drain line breaks
Investigate Kelvin Canyon Spring
  Flow diverted since 2019 fire hydrant break at Del Cero Park
  Working with RPV Public Works to repair stream bed
Participating in Landslide Meetings
  Cal Water: Tuesdays
  RPV Landslide Working Group
  LA Public Works for Altamira Canyon
Plans:
  Start operation of 6 new wells
  Work on Kelvin Spring and Altamira Canyons
  WW 2 Broken drain line
  WW 7 Trouble shooting
  WW 3 Electrical issue
  WW 21 Trouble shooting

## Slide 2: Four RPV Wells Drilled
Friday: Installing 8” PVC
Casing
4 RPV City Wells drilled and developed
  Well 9 water depth: 114’3”
  Well 18 water depth: 52’6”
  Well 19 water depth: 53’
  Well 20 water depth: 51’5”
Monday Unloading drill rig
Setting up on bluff
Sonic Mud Drilling Rig
Well # 18
Well # 20
Well # 19
Well # 9
Well 18 &20 drain lines and electrical complete. Coordinating with SCE for power
Installing pumps next week
Well 19 & 9 hookups in work

## Slide 3: PVDS Culvert Repair Completed
Multiple cracks in PVDS Culver
  Cracks range from 1” to 6” at pipe section joints
  11 large cracks to be repaired with expansion joints
PVDS Culvert Repair
  Remove 6” thick concrete liner at cracked joints
  Install simple metal expansion joint
  Replace concrete liner over joint
Cracks at pipe joints
Most damage under
PVDS
Broken Security
Gate & hole at
exit
Before
Expansion Joint
After