## Slide 1
ACLAD Summary Report March 9, 2022
Chart: 
| 44571 | 44572 | 44586 | 44594 | 44600 | 44607 | 44614 | 44621 | 44628
Narcissa/Gingerroot 1 | 20863.0714 | 21829.5714 | 13171.4286 | 7020 | 17153.3333 | 6381.4286 | 0 | 20680 | 17455.6522
lower Narcissa 2 | 5108.5714 | 5004.2857 | 5014.2857 | 4977.1429 | 5526.6667 | 5100 | 5948.5714 | 2051.4286 | 4944.2857
Narcissa/Figtree 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Beanfield 11 | 11344.7143 | 11402.5714 | 11142.8571 | 10955 | 10805 | 10871.5714 | 11198.7143 | 9065.7391 | 11665.4286
upper Gingerroot 12 | 17531.4286 | 17685.7143 | 16897.8571 | 14955.7143 | 20133.3333 | 16454.2857 | 15795.7143 | 17100.8696 | 17227.1429
King/Sweetbay 13 | 9997.1429 | 10087.1429 | 9845 | 7271.25 | 12960 | 9712.8571 | 10105.7143 | 3455.6522 | -5872.8571
Narcissa/Vanderlip 15 | 1779.5714 | 1750.1429 | 1786.1429 | 3206 | 15472.3333 | 13292 | 0 | 12623.6522 | 21339.7143
Petak/Sweetbay 16 | 6590 | 7081.4286 | 9236.4286 | 9235 | 8160 | 12240 | 5170 | 8450.4348 | 8801.4286
Thyme 17 | 1267.8571 | 1001.4286 | 952.8571 | 941.25 | 911.6667 | 905.7143 | 990 | 944.3478 | 868.5714
End of Narcissa 19 | 2570.7143 | 2144.2857 | 2108.5714 | 1638.5714 | 1900 | 1427.1429 | 1317.1429 | 1109.5652 | 794.2857
Sweetbay Yamaguchi | 3961.4286 | 3825.7143 | 3851.4286 | 3818.75 | 3618.3333 | 3700 | 3582.8571 | 4266.087 | 3494.2857
Lower Figtree 3 | 9602.1429 | 10057.1429 | 8330.7143 | 7102.8571 | 7851.6667 | 5637.1429 | 5240 | 3880 | 3845.7143

## Slide 2: ACLAD STATUS
CURRENTLY PUMPING 77,224 GALLONS PER DAY
Well #15 pump replaced
Fixed leak in 4” drain pipe across PVDS
Received 3” System Output Meter
Received well camera and found buckle in Well #7 at aprox 125’
Well #13 Pump? Failed last week
Well #8 (mid-sweetbay) very low flow. Turned off to diagnose cause
ACLAD Near-term Plan
  Install Output Meter across PVDS
  Replace pump in Well #7 (Narcissa by Figtree)
  Diagnose well #13 Failure
  Check out pump in well #2 (lower Narcissa), gradually decreasing output

## Slide 3: Video of Well #7

## Slide 4: Weekly Well Monitoring (gallons per day)
2-Feb
8-Feb
15-Feb
22-Feb
1-Mar
8-Mar
 | Narcissa/Gingerroot | lower Narcissa | Narcissa/Figtree | Beanfield | upper Gingerroot | King/Sweetbay | Narcissa/Vanderlip
 | 1 | 2 | 7 | 11 | 12 | 13 | 15
Petak/Sweetbay | Thyme | End of Narcissa | Sweetbay | Lower Figtree | Mid Sweetbay | Total GPD
16 | 17 | 19 | Yamaguchi | 3 | 8 | Total
9,235 | 941 | 1,639 | 3,819 | 7,103 | 5,720 | 60,200
8,160 | 912 | 1,900 | 3,618 | 7,852 | 1,402 | 93,022
12,240 | 906 | 1,427 | 3,700 | 5,637 | 1,390 | 76,385
5,170 | 990 | 1,317 | 3,583 | 5,240 | 1,397 | 50,526
8,450 | 944 | 1,110 | 4,266 | 3,880 | 694 | 75,482
8,801 | 869 | 794 | 3,494 | 3,846 | 0 | 77,224
2-Feb | 7,020 | 4,977 | 0 | 10,955 | 14,956 | 7,271 | 3,206
8-Feb | 17,153 | 5,527 | 0 | 10,805 | 20,133 | 12,960 | 15,472
15-Feb | 6,381 | 5,100 | 0 | 10,872 | 16,454 | 9,713 | 13,292
22-Feb | 0 | 5,949 | 0 | 11,199 | 15,796 | 10,106 | 0
1-Mar | 20,680 | 2,051 | 0 | 9,066 | 17,101 | 3,456 | 12,624
8-Mar | 17,456 | 4,944 | 0 | 11,665 | 17,227 | 0 | 21,340