## Slide 1: 6/20/2025 Status 85,000 to 100,000 GPD
11 wells are pumping 85 to 100K Gallons per Day
DDWs
  10 DDWs, 2 Monitoring Wells, and one bonus well completed
  8 of 10 Planned DDWs are Operational
    2 need final connection of East Drain line
    Early Pumping Rates variable
  DDW 16 running on hosted Solar Power
Original Wells
  5 of 12 Original Wells Operational
    2 need repair
    4 wells below PVDS need power
Added East Drain line
  3000’ of 4” drainage line installed along Sweetbay
  Attached to abandoned RPV drain line from Narcissa to Ocean
  East Drain line nearly doubles ACLAD capacity
ACLAD continues to have strong volunteer support
    Over a dozen members of the “Well Team” turn the generators on/off daily
    Several volunteers repair and change oil on generators

## Slide 2: ACLAD Well Status 6.20.25
WW XX - Operating Wells
- existing drainage lines
- new drainage lines
- Operating DDW
  - Drilled and Finalizing
  - Proposed DDW
WW12
WW1
WW15
WW11
WW17
WW20
WW6
WW18
WW3
WW13
DDW24
DDW28
DDW26
DDW16
DDW21
DDW25
DDW8
DDW22
DDW29
WW10
WW30
WW31
DDW27
East Drainage
West Drainage
DDW27
Location | DDW Well | Status | Output | Drainage
Mid Sweetbay | 8 | Drain line connect | ? | W
Petak Sweetbay | 16 | Operating | 6 KGPD | E
End of Sweetbay | 21 | Drain line connect | ? | E
End of Narcissa | 22 | Operating | ? | E
38 Narccissa | 24 | Operating | 5 KGPD | W
PBRC | 25 | Operating | 17.6 KGPD | W
Barth Sweetbay | 26 | Operating | 4.5 KGPD | W
Thyme | 27 | Operating | 11.3 KGPD | W
Parks Cinnamon | 28 | Operating | 3 KGPD | E
Douglas Narcissa | 29 | Operating | ? | E
 | Original Wells |  | K GPD | 
Narcissa and Ginger Root | WW 1 | Operating | 11 | W
Figtree | WW 3 | Replacing pump | 0 | W
CloveTree | WW6 | Dry | 0.2 | 
Figtree | WW10 | Trouble shooting | 0 | W
Bean Field | WW11 | Operating | 11 | E
Ginger Root | WW12 | Operating | 7 | W
Sweetbay | WW 13 | Operating | 16 | 
Narcissa and Ginger Root | WW15 | Operating | 15 | E
Petak Sweetbay | WW16a | Replacing pump | 0 | E
Thyme | WW17 | Replacing pump | 0 | W
Upper Cinnamon | WW 30 | Partial Shear | ~5 GPM @ 108’ | W
York | WW31 | Planned | ~ 180'x4" auger well | W